SECTION 22 00 00

PENETRATION FIRESTOPPING FOR PLUMBING

# GENERAL

## RELATED DOCUMENTS

### Drawings and general provisions of Contract, including General and Supplementary Conditions and Division-1 Specification Section, apply to work specified in this section.

## DEFINITIONS

### Firestopping:  Material or combination of materials used to retain integrity of fire-rated construction by maintaining an effective barrier against the spread of flame, smoke, and hot gases through penetrations in fire rated wall and floor assemblies.

## GENERAL DESCRIPTION OF THE WORK OF THIS SECTION

Only tested firestop systems shall be used in specific locations as follows:

### Penetrations for the passage of duct, piping, and other mechanical equipment through fire-rated vertical barriers (walls and partitions), horizontal barriers (floor/ceiling assemblies), and vertical service shaft walls and partitions.

### Repetitive plumbing penetrations in fire-rated floor assemblies.  Penetrations exist for the installation of tubs, showers, aerators and other plumbing fixtures.

## RELATED WORK OF OTHER SECTIONS

### Coordinate work of this section with work of other sections as required to properly execute the work and as necessary to maintain satisfactory progress of the work of other sections, including:

#### Section 03 30 00 - Cast-In-Place Concrete

#### Section 04 20 00 - Masonry Work

#### Section 07 84 43 - Joint Firestopping

#### Section 07 90 00 - Joint Protection

#### Section 09 20 00 - Plaster and Gypsum Board

#### Section 09 29 00 - Gypsum Board

#### Section 13 48 00 - Sound, Vibration and Seismic Control

#### Section 21 00 00 - Fire Suppression

#### Section 22 00 00 - Plumbing

#### Section 23 00 00 - Heating, Ventilating, and Air Conditioning

#### Section 26 00 00 - Electrical

## REFERENCES

### Test Requirements: CAN/ULC-S115 2015 or CAN/ULC-S115: 2018, " STANDARD METHOD OF FIRE TESTS OF FIRESTOP SYSTEMS.

### Underwriters Laboratories of Canada (ULC) of Scarborough runs CAN/ULC-S115:2018  under their designation of ULC-S115:2018 and publishes the results in their "FIRE RESISTANCE RATINGS DIRECTORY" that is updated annually.

### Underwriters Laboratories (UL) of Northbrook, IL runs ASTM E-814 under their designation of UL 1479 and publishes the results in their "FIRE RESISTANCE DIRECTORY" that is updated annually. UL tests that meet the requirements of ULC-S115-M are given a cUL listing and are published by UL in their “Products Certified for Canada (cUL) Directory.

### Omega Point Laboratories runs ASTM E-814 and publishes the results annually in their “Omega Point Laboratories Directory”.

### Canada Green Building Council (CaGBC). LEED Canada V4.0- Building Design and Construction, Interior Design + Construction (ID+C)

### Health Canada/ Workplace Hazardous Material Information System (WHMIS).

### Inspection Requirements:  ASTM E 2174, “Standard Practice for On-site Inspection of Installed Fire Stops.”, and ASTM E2393 Standard Practice for On-Site Inspection of Installed Fire Resistive Joint Systems and Perimeter Fire Barriers.

### Test Requirements: ASTM E 2307, “Standard Test Method for Determining Fire Resistance of Perimeter Fire Barrier Systems Using Intermediate-Scale, Multi-story Test Apparatus”.

### International Firestop Council Guidelines for Evaluating Firestop Systems Engineering Judgments.

### CAN/ULC-S102:2018, Standard Test Method for Surface Burning Characteristics of Building Materials and CAN/ULC-S101 Fire Endurance Tests of Building Construction and Materials.

### ASTM D6904, “Standard Practice for Resistance to Wind Driven Rain for Exterior Coatings Applied on Masonry”.

### ASTM C 679, “Standard Test Method for Tack-Free Time of Elastomeric Sealants”.

### All major building codes:  NBC, OBC, BCBC, and ABC.

Note to specifier: Retain or delete building codes listed above as applicable

### NFPA 101 - Life Safety Code.

## QUALITY ASSURANCE

### Fire-Test-Response Characteristics:  Provide through-penetration fire stop systems and fire-resistive joint systems that comply with specified requirements of tested systems.

### Firestop System installation must meet requirements of CAN/ULC-S115:2018 tested assemblies that provide a fire rating as shown in Section 2.1 Clauses 4, 5, 6 & 7 below.

### Proposed firestop materials and methods shall conform to applicable governing codes having local jurisdiction.

### Firestop Systems do not reestablish the structural integrity of load bearing partitions/assemblies, or support live loads and traffic.  Installer shall consult the structural engineer prior to penetrating any load bearing assembly.

### For those firestop applications that exist for which no ULC or cUL tested system is available through a manufacturer, a manufacturer's engineering judgment derived from similar ULC or cUL system designs or other tests will be submitted to local authorities having jurisdiction for their review and approval prior to installation.  Engineering judgment drawings must follow requirements set forth by the International Firestop Council

## SUBMITTALS

### Submit Product Data:  Manufacturer's specifications and technical data for each material including the composition and limitations, documentation of ULC or cUL firestop systems to be used and manufacturer's installation instructions to comply with Section 1300.

### Manufacturer's engineering judgment identification number and drawing details when no ULC or cUL system is available for an application.  Engineered judgment must include both project name and contractor’s name who will install firestop system as described in drawing.

### Submit material safety data sheets provided with product delivered to job-site.

### Submit shop drawings in accordance with section 01 33 22 – Submittals:

#### Submit complete cUL, ULC or equivalent approved systems for all applications.

### Submit certificate by firestopping manufacturer proving that the products supplied comply with LEED requirements for indoor environmental quality credit including printed statement of VOC.

## INSTALLER QUALIFICATIONS

### Engage an experienced Installer who is certified, licensed, or otherwise qualified by the firestopping manufacturer as having the necessary training to install manufacture’s products per specified requirements.  A supplier’s willingness to sell its firestopping products to the Contractor or to an Installer engaged by the Contractor does not in itself confer qualification on the buyer.

Note to Specifier: Section 2 and Section 3 are suggested if the owner or architect require a specialty contractor to firestop the entire project or a portion of it

### Installation Responsibility: assign installation of through-penetration firestop systems and fire-resistive joint systems in Project to a single sole source firestop specialty contractor.

### The work is to be installed by a contractor with at least one of the following qualifications if pre-formed devices are not used as defined in section 2.3 :

#### FM 4991 Approved Contractor

#### ULC Approved Contractor

#### Hilti Accredited Fire Stop Specialty Contractor

### Installer shall have not less than 3 years experience with fire stop installation.

## DELIVERY, STORAGE, AND HANDLING

### Deliver materials undamaged in manufacturer's clearly labeled, unopened containers, identified with brand, type, and ULC or cUL label where applicable.

### Coordinate delivery of materials with scheduled installation date to allow minimum storage time at job-site.

### Store materials under cover and protect from weather and damage in compliance with manufacturer's requirements.

### Comply with recommended procedures, precautions or remedies described in material safety data sheets as applicable.

### Do not use damaged or expired materials.

## PROJECT CONDITIONS

### Do not use materials that contain flammable solvents.

### Scheduling

#### Schedule installation of CAST IN PLACE firestop devices after completion of floor formwork, metal form deck, or composite deck but before placement of concrete.

#### Schedule installation of Drop-In firestop devices after placement of concrete but before installation of the pipe penetration. Diameter of sleeved or cored hole to match the listed system for the device.

#### Schedule installation of other firestopping materials after completion of penetrating item installation but prior to covering or concealing of openings.

#### Schedule installation of preformed joint materials to be installed with the metal framing

### Verify existing conditions and substrates before starting work.  Correct unsatisfactory conditions before proceeding.

### Weather conditions:  Do not proceed with installation of firestop materials when temperatures exceed the manufacturer's recommended limitations for installation printed on product label and product data sheet.

### During installation, provide masking and drop cloths to prevent firestopping materials from contaminating any adjacent surfaces.

# PRODUCTS

## PERFORMANCE REQUIREMENTS

### Provide firestopping composed of components that are compatible with each other, the substrates forming openings, and the items, if any, penetrating the firestopping under conditions of service and application, as demonstrated by the firestopping manufacturer based on testing and field experience.

### Provide components for each firestopping system that are needed to install fill material.  Use only components specified by the firestopping manufacturer and approved by the qualified testing agency for the designated fire-resistance-rated systems.

### For combustible pipe penetrations through a Fire Separation provide a firestop system with a “F” Rating as determined by ULC or cUL which is equal to the fire resistance rating of the construction being penetrated.

### Penetrations in firewall or a horizontal fire separation above a garage: Provide firestopping with ratings determined in accordance with CAN/ULC-S115. provide a firestop system with a “FT” Rating as determined by cUL which is equal to the fire resistance rating of the construction being penetrated.

### Penetrations by polypropylene pipes through any fire separation required to have a fire resistance rating shall be protected by a firestop system with an “FT” rating.

### W-Rating: Class 1 rating in accordance with water leakage test per UL1479.

Note to specifier: Retain or delete W-rating listed below if horizontal assemblies require water resistance. W-ratings are not required by the NBC.

### Provide a firestop system with an Assembly Rating as determined by ULC-S115 which is equal to the time rating of construction joint assembly.

### Penetrations or joints in Smoke Barriers: Provide firestopping with ratings determined in accordance with CAN/ULC-S115.

#### L-Rating: Not exceeding 5.0 cfm/sq. ft. of penetration opening or joints at both ambient and elevated temperatures.

Note to Specifier: Mold Resistance - On a rating scale from zero to four (0-4), a value of zero (0) indicates No Growth observed; a value of one (1) indicates Traces of Growth observed (less than 10%); a value of four (4) indicates Heavy Growth (60% to complete coverage)

### Mold Resistance: Provide penetration firestopping with mold and mildew resistance rating of 0 as determined by ASTM G21.

### Rain and water resistance: provide perimeter joint sealant tested in accordance with ASTM D 6904 with less than 1 hour tack free time as tested in accordance with ASTM C 679.

## ACCEPTABLE MANUFACTURERS

### Subject to compliance with through penetration firestop systems and joint systems listed in the U.L.C Fire Resistance Directory – Volume III or UL Products Certified for Canada (cUL) Directory, provide products of the following manufacturers as identified below:

#### Basis of Design:
Hilti (Canada) Corporation, Oakville, Ontario
1-800-363-4458
www.hilti.ca

#### Substitution requests shall be considered in accordance with contract provisions

## MATERIALS

### Use only firestop products that have been ULC or cUL tested for specific fire-rated construction conditions conforming to construction assembly type, penetrating item type, annular space requirements, and fire-rating involved for each separate instance.

### Accessories: provide components for each firestopping and smoke seal systems that are needed to install fill materials. Use only components specified by firestopping material manufacturer and approved by the qualified testing agency. Accessories include, but are not limited to, the following items:

#### Permanent forming, damming and backing material.

#### Temporary forming material.

### Pre-formed firestop devices for use with non-combustible and combustible pipes (closed and open systems) penetrating concrete floors and/or gypsum walls, the following products are acceptable:

#### Hilti Tub Box Kit (CP 681) for use with tub installations.

#### Hilti Cast-In Place Firestop Device (CP 680-PX) for use with XFR pipe

#### Hilti Cast-In Place Firestop Device (CP 680-M) for use with noncombustible penetrants.

#### Hilti Firestop Drop-In Device (CFS-DID) for use with noncombustible and combustible penetrants.

#### Hilti Cast-in Firestop sleeve (CFS-CID MD P) and (CFS-CID MD M) for use with combustible and noncombustible pipes through metal deck.

### Sealants or caulking materials for use with non-combustible items including steel pipe, copper pipe, rigid steel conduit and electrical metallic tubing (EMT), the following products are acceptable:

#### Hilti Intumescent Firestop Sealant (FS-ONE MAX)

#### Hilti Fire Foam (CP 620)/CP 660

#### Hilti Flexible Firestop Sealant (CP 606)

#### Hilti Firestop Silicone Sealant Gun Grade (CFS-S SIL GG)

#### Hilti Firestop Silicone Sealant Self Leveling (CFS-S SIL SL)

### Intumescent sealants or caulking materials for use with combustible items (penetrants consumed by high heat and flame) including insulated metal pipe, PVC jacketed, flexible cable or cable bundles and plastic pipe, the following products are acceptable:

#### Hilti Intumescent Firestop Sealant (FS-ONE MAX)

### Firestop collar or wrap devices attached to assembly around combustible plastic pipe (closed and open piping systems) tested to 50 Pa. pressure differential, the following products are acceptable:

#### Hilti Firestop Collar (CP 643N)

#### Hilti Wrap Strips (CP 648E/648S)

# EXECUTION

## PREPARATION

### Verification of Conditions:  Examine areas and conditions under which work is to be performed and identify conditions detrimental to proper or timely completion.

#### Verify penetrations are properly sized and in suitable condition for application of materials.

#### Surfaces to which firestop materials will be applied shall be free of dirt, grease, oil, rust, laitance, release agents, water repellents, and any other substances that may affect proper adhesion.

#### Provide masking and temporary covering to prevent soiling of adjacent surfaces by firestopping materials.

#### Comply with manufacturer's recommendations for temperature and humidity conditions before, during and after installation of firestopping.

#### Do not proceed until unsatisfactory conditions have been corrected.

## COORDINATION

### Coordinate construction of openings, penetrations to ensure that the fire stop systems are installed according to specified requirements.

### Coordinate sizing of sleeves, openings, core-drilled holes, or cut openings to     accommodate through-penetration fire stop systems.

### Coordinate fire stopping with other trades so that obstructions are not placed in the way      prior to the installation of the fire stop systems.

### Do not cover up through-penetration fire stop and joint system installations that will become concealed behind other construction until each installation has been examined by the building inspector.

## INSTALLATION

### Regulatory Requirements: Install firestop materials in accordance with ULC Fire Resistance Directory or UL Products Certified for Canada (cUL) Directory or Omega Point Laboratories Directory.

### Manufacturer's Instructions: Comply with manufacturer's instructions for installation of through-penetration and construction joint materials.

#### Seal all holes or voids made by penetrations to ensure an air and water resistant seal.

#### Consult with mechanical engineer, project manager, and damper manufacturer prior to installation of ULC or cUL firestop systems that might hamper the performance of fire dampers as it pertains to duct work.

#### Protect materials from damage on surfaces subjected to traffic.

## FIELD QUALITY CONTROL

### Examine sealed penetration areas to ensure proper installation before concealing or enclosing areas.

### Keep areas of work accessible until inspection by applicable code authorities.

### Inspection of through-penetration firestopping shall be performed in accordance with ASTM E 2174, “Standard Practice for On-Site Inspection of Installed Fire Stops” or other recognized standard.

### Perform under this section patching and repairing of firestopping caused by cutting or penetrating of existing firestop systems already installed by other trades.

### Manufacturer’s Field Services: The manufacturer’s representative to be present during the first installation of every first firestop system. The manufacturer’s technical representative to provide periodic walk-through. After every site visit the manufacturer’s technical representative to submit site reports to indicate application reviewed, location and installer. Contractor to submit site reports by manufacturer to consultant within one week of each visit

## IDENTIFICATION & DOCUMENTATION

### The firestop contractor is to supply documentation for each single application addressed.        This documentation is to identify each penetration location on the entire project.

### The Documentation Form for through penetrations is to include:

#### A Sequential Location Number

#### The Project Name

#### Date of Installation

#### Detailed description of the penetrations location

#### Tested System or Engineered Judgment Number

#### Type of assembly penetrated

#### A detailed description of the size and type of penetrating item

#### Size of opening

#### Number of sides of assemblies addressed

#### Hourly rating to be achieved

#### Installers Name

### Copies of these documents are to be provided to the general contractor at the completion of the project.

### Identify through-penetration firestop systems with pressure-sensitive, self-adhesive, preprinted vinyl labels.  Attach labels permanently to surfaces of penetrated construction on both sides of each firestop system installation where labels will be visible to anyone seeking to remove penetrating items or firestop systems.  Include the following information on labels:

#### The words:  "Warning -Through Penetration Firestop System-Do Not Disturb. Notify   Building Management of Any Damage."

#### Contractor's Name, address, and phone number.

#### Through-Penetration firestop system designation of applicable testing and   inspecting agency.

#### Date of Installation.

#### Through-Penetration firestop system manufacturer's name.

#### Installer's Name.

## ADJUSTING AND CLEANING

### Remove equipment, materials and debris, leaving area in undamaged, clean condition.

### Clean all surfaces adjacent to sealed holes and joints to be free of excess firestop materials and soiling as work progresses.

## LABOR USE TO INSTALL FIRESTOP SYSTEMS

### To ensure complete harmony on the project site, the installation of each scope of work is to be performed jurisdictionally correct per existing trade agreements.

END OF SECTION