Note to specifier:  The following specification text can be incorporated within relevant specification sections where a pre-formed sleeve solution is desired for firestopping protection of cable pathways.  Please refer to the product technical data at www.hilti.com or www.hilti.ca.

Applicable Specification Sections:

Section 07 84 00	Firestopping

Section 07 84 13	Penetration Firestopping

Section 26 00 00	Penetration Firestopping for Electrical

Section 27 05 37	Firestopping, Smoke & Acoustical Sealing for Communications Systems

PART 2 – PRODUCTS

2.01	PERFORMANCE REQUIREMENTS

- Provide a fire-rated cable pathway device whenever single and/or bundled low-voltage cables penetrate fire rated concrete, masonry and drywall walls and floors, where frequent cable additions and changes may occur. The fire-rated cable management device shall contain integrated intumescent firestop wrap strip materials sufficient to maintain the hourly rating of the barrier being penetrated. The device shall be capable of being easily ganged together with any combination of compatible sleeves using gang plate systems. The fire-rated cable management device shall consist of a bare metal housing and frame(s) to enable grounding for electrical continuity. The device shall provide airflow containment sufficient to achieve the L-Rating requirements of the barrier type.

  - Round fire-rated cable management device: The device shall consist of a corrugated steel tube with zinc coating, contain and inner plastic housing, intumescent material rings, and inner fabric smoke seal membrane. The device shall contain a smoke seal fabric membrane or intumescent firestop plugs sufficient to achieve the L-Rating.  Install device per the manufacturer’s published installation instructions.

  - Rectangular fire-rated cable management device: The device shall consist of a rectangular galvanized steel sleeve with a symmetrical half-shell design for retrofit capabilities. The device shall consist of an inner and outer layer of brushes on both ends of the device sufficient to achieve the L-Rating. The device shall be capable of being easily ganged together using gang plate or floor grid systems with ganging clips.  Install device per the manufacturer’s published installation instructions.

2.02	ACCEPTABLE MANUFACTURERS

- Subject to compliance with through penetration firestop systems (XHEZ), joint systems (XHBN), and perimeter firestop systems (XHDG) listed in Volume 2 of the UL Fire Resistance Directory or other qualified tested firestop systems; provide products of the following manufacturers as identified below:

- Basis of Design:

Hilti, Inc., Plano, Texas

800-879-8000

www.us.hilti.com

- Substitution requests shall be considered in accordance with contract provisions.

2.03	MATERIALS

- Subject to compliance with requirements, provide (one of) the following product(s) (or approved equivalent):

- Round fire-rated cable management device for use with new and/or existing cable penetrations in walls and floors:

  - Hilti CP 653 BA Firestop Speed Sleeve

  - Hilti CFS-SL GA L Firestop Speed Sleeve

- Rectangular fire-rated cable management device for use with new and/or existing cable penetrations in walls and floors:

- Hilti CFS-MSL Modular Firestop Sleeve System

    - CFS-MSL S 3X2”

    - CFS-MSL M 3X4”

    - CFS-MSL L 6X4”

END OF SECTION